## Data
Weather data
| No. days | Cumulative seconds | Average outdoor temperature (°C) | Maximum outdoor temperature (°C) | Minimum outdoor temperature (°C) | Max 6h average radiation (south) [W] | Average monthly radiation (south) [W] | Max 6h average radiation (north) [W] | Average monthly radiation (north) [W]
January | 31 | 2678400 | 3.6 | 14.3 | -7.6 | 718.39 | 41.31 | 66.64 | 7.76
February | 28 | 5097600 | 4.5 | 14.7 | -5.5 | 734 | 69.09 | 101.6 | 13.85
March | 31 | 7776000 | 7.3 | 17.9 | -2.1 | 729.7 | 80.69 | 140.1 | 23.61
April | 30 | 10368000 | 9.8 | 19.9 | -0.7 | 636.6 | 92.05 | 169.8 | 38.42
May | 31 | 13046400 | 13.9 | 26.3 | 3.6 | 574.964 | 87.5 | 234.6207 | 58.14
June | 30 | 15638400 | 16.6 | 27.5 | 7.4 | 534.0189 | 82.42 | 242.5054 | 57.57
July | 31 | 18316800 | 18.1 | 29.4 | 10.2 | 555.0326 | 83.65 | 257.5101 | 58.42
August | 31 | 20995200 | 18.7 | 29.3 | 11 | 602.1357 | 98.07 | 177.7041 | 54.24
September | 30 | 23587200 | 15.2 | 29.1 | 6.9 | 777.9027 | 94.15 | 160.0384 | 27.75
October | 31 | 26265600 | 11.4 | 21.1 | 3.9 | 768.97 | 87.71 | 107.8594 | 22.58
November | 30 | 28857600 | 6.7 | 15.8 | -1.5 | 662.3044 | 55.34 | 70.4642 | 8.98
December | 31 | 31536000 | 4 | 13.4 | -4.8 | 519.4114 | 30.9 | 47.1631 | 6.27
Air properties
Density | 1.225 | kg/m3
Heat capacity | 1005 | J/kg/K
Building data
Area zone north | 500 | m²
Area zone south | 500 | m²
Building lenght | 44.7214 | m
Building width | 22.3607 | m
Building height | 2.7 | m
Window-to-wall ratio | 40%
A_roof | 1000 | m²
A_floor | 1000 | m²
A_envelope | 362.243 | m²
A_wall_north | 72.4486 | m²
A_wall_east | 60.3738 | m²
A_wall_south | 72.4486 | m²
A_wall_west | 60.3738 | m²
A_windows_north | 48.2991 | m²
A_windows_south | 48.2991 | m²
Occupants | 60 | p
Set-points
TdesHea | 21 | °C
TdesCoo | 24.5 | °C
| Building 1 | Building 2
U_roof | 0.16 | 0.32 | W/(m²K)
U_walls | 0.2 | 0.51 | W/(m²K)
U_floor | 0.16 | 0.32 | W/(m²K)
U_windows | 1.1 | 5.95 | W/(m²K)
g_windows | 0.42 | 1 | -
n50 | 1.3 | 8.2 | 1/h
| Building evaluated |  | 1
| Building 1 | Building 2 | Evaluated
UA_floor | 160 | 320 | 160
UA_roof | 160 | 320 | 160
UA_wall_noth | 14.4897 | 36.9488 | 14.4897
UA_wall_east | 12.0748 | 30.7907 | 12.0748
UA_wall_south | 14.4897 | 36.9488 | 14.4897
UA_wall_west | 12.0748 | 30.7907 | 12.0748
UA_windows_north | 53.129 | 287.3795 | 53.129
UA_windows_south | 53.129 | 287.3795 | 53.129
gA_windows_north | 20.2856 | 48.2991 | 20.2856
gA_windows_south | 20.2856 | 48.2991 | 20.2856
n50 | 1.3 | 8.2 | 1.3
Occupants | 60 | 60 | 60
Auxiliary parameters
Average yearly temperature | 10.8167 | °C
Total building UA (without floor) | 319.3869 | W/(m²K)
Gain per occupant | 73 | W

## Building loads
PEAK LOADS |  |  | Heating loads |  |  |  | Cooling loads
| Hea? | Coo? | Transmission losses (W) | Infiltration losses (W) | Total heating (W) | Heating per m² (W) | Transmission gains (W) | Radiation gains (W) | Infiltration losses (W) | Internal gains (W) | Total cooling (W) | Cooling per m² (W)
January | TRUE | FALSE | 10763.7994 | 1716.496 | 12480.2954 | 12.4803 | 0 | 15924.8114 | 0 | 4380 | 0 | 0
February | TRUE | FALSE | 10093.0869 | 1590.4596 | 11683.5465 | 11.6835 | 0 | 16950.6546 | 0 | 4380 | 0 | 0
March | TRUE | FALSE | 9007.1713 | 1386.4006 | 10393.572 | 10.3936 | 0 | 17644.4224 | 0 | 4380 | 0 | 0
April | TRUE | TRUE | 8560.0296 | 1302.3764 | 9862.406 | 9.8624 | 0 | 16358.3148 | 0 | 4380 | 20738.3148 | 20.7383
May | FALSE | TRUE | 7186.6658 | 1044.3018 | 0 | 0 | 574.8965 | 16422.919 | 108.0312 | 4380 | 21485.8467 | 21.4858
June | FALSE | TRUE | 5972.9955 | 816.2359 | 0 | 0 | 958.1608 | 15752.2679 | 180.052 | 4380 | 21270.4807 | 21.2705
July | FALSE | TRUE | 5078.7121 | 648.1873 | 0 | 0 | 1564.9959 | 16482.9243 | 294.085 | 4380 | 22722.0052 | 22.722
August | FALSE | TRUE | 4823.2026 | 600.1734 | 0 | 0 | 1533.0572 | 15819.5254 | 288.0833 | 4380 | 22020.6659 | 22.0207
September | FALSE | TRUE | 6132.689 | 846.2445 | 0 | 0 | 1469.1799 | 19026.7061 | 276.0798 | 4380 | 25151.9658 | 25.152
October | TRUE | TRUE | 7090.8498 | 1026.2966 | 8117.1463 | 8.1171 | 0 | 17787.0179 | 0 | 4380 | 22167.0179 | 22.167
November | TRUE | FALSE | 8815.5392 | 1350.3902 | 10165.9294 | 10.1659 | 0 | 14864.6565 | 0 | 4380 | 0 | 0
December | TRUE | FALSE | 9869.516 | 1548.4475 | 11417.9635 | 11.418 | 0 | 11493.3101 | 0 | 4380 | 0 | 0
[5 empty] | MAX | 12480.2954 |  |  |  |  | MAX | 25151.9658
MONTHLY LOADS |  |  | Heating loads |  |  |  | Cooling loads
| Hea? | Coo? | Transmission losses (W) | Infiltration losses (W) | Total heating (W) | Heating per m² (W) | Transmission gains (W) | Radiation gains (W) | Infiltration losses (W) | Internal gains (W) | Total cooling (W) | Cooling per m² (W)
January | TRUE | FALSE | 7186.6658 | 1044.3018 | 8230.9676 | 8.231 | 0 | 995.4148 | 0 | 4380 | 0 | 0
February | TRUE | FALSE | 6899.2176 | 990.2862 | 7889.5038 | 7.8895 | 0 | 1682.4884 | 0 | 4380 | 0 | 0
March | TRUE | FALSE | 6004.9342 | 822.2376 | 6827.1718 | 6.8272 | 0 | 2115.789 | 0 | 4380 | 0 | 0
April | TRUE | TRUE | 5206.4669 | 672.1943 | 5878.6611 | 5.8787 | 0 | 2646.6634 | 0 | 4380 | 7026.6634 | 7.0267
May | FALSE | TRUE | 3896.9805 | 426.1231 | 0 | 0 | 0 | 2954.396 | 0 | 4380 | 7334.396 | 7.3344
June | FALSE | TRUE | 3034.6358 | 264.0763 | 0 | 0 | 0 | 2839.7824 | 0 | 4380 | 7219.7824 | 7.2198
July | FALSE | TRUE | 2555.5554 | 174.0503 | 0 | 0 | 0 | 2881.9764 | 0 | 4380 | 7261.9764 | 7.262
August | FALSE | TRUE | 2363.9233 | 138.0399 | 0 | 0 | 0 | 3089.7011 | 0 | 4380 | 7469.7011 | 7.4697
September | FALSE | TRUE | 3481.7775 | 348.1006 | 0 | 0 | 0 | 2472.8157 | 0 | 4380 | 6852.8157 | 6.8528
October | TRUE | TRUE | 4695.4478 | 576.1665 | 5271.6143 | 5.2716 | 0 | 2237.2998 | 0 | 4380 | 6617.2998 | 6.6173
November | TRUE | FALSE | 6196.5664 | 858.248 | 7054.8144 | 7.0548 | 0 | 1304.7704 | 0 | 4380 | 0 | 0
December | TRUE | FALSE | 7058.9111 | 1020.2948 | 8079.2059 | 8.0792 | 0 | 754.0161 | 0 | 4380 | 0 | 0
[5 empty] | MAX | 8230.9676 |  |  |  |  | MAX | 7469.7011
Note on D2: Iago Cupeiro: Be careful with the ground losses
Note on H2: Iago Cupeiro: Note that here we do not consider the ground (as it is colder than the environment), which would be losses instead of gains. The minimum gains are 0

## Ground loads
COP = | 4.9
GROUND MONTHLY LOADS |  |  |  | GROUND YEARLY LOAD |  | GROUND PEAK LOADS
| Heating (W) | Cooling (W) | No.days | Heating energy (W.day) | Cooling energy (W.day) | Heating | Cooling
January | 6551.1783 | 0 | 31 | 203086.5275 | 0 | 9933.2964 | 0
February | 6279.401 | 0 | 28 | 175823.227 | 0 | 9299.1492 | 0
March | 5433.8714 | 0 | 31 | 168450.0149 | 0 | 8272.4348 | 0
April | 4678.9344 | 7026.6634 | 30 | 140368.0315 | 210799.901 | 7849.6701 | 20738.3148
May | 0 | 7334.396 | 31 | 0 | 227366.2775 | 0 | 21485.8467
June | 0 | 7219.7824 | 30 | 0 | 216593.4708 | 0 | 21270.4807
July | 0 | 7261.9764 | 31 | 0 | 225121.2692 | 0 | 22722.0052
August | 0 | 7469.7011 | 31 | 0 | 231560.7329 | 0 | 22020.6659
September | 0 | 6852.8157 | 30 | 0 | 205584.471 | 0 | 25151.9658
October | 4195.7747 | 6617.2998 | 31 | 130069.0145 | 205136.2933 | 6460.5859 | 22167.0179
November | 5615.0563 | 0 | 30 | 168451.6904 | 0 | 8091.2499 | 0
December | 6430.3884 | 0 | 31 | 199342.0397 | 0 | 9087.7669 | 0
MAX | 6551.1783 | 7469.7011 | SUM | 1185590.5455 | 1522162.4157 | MAX HEA | MAX COO
|  |  | UNBALANCE | 922.1147 | W | 9933.2964 | 25151.9658